## Slide 1
Office power and data plan
Proposed outlet locations for the existing furniture and new bar fridge
Proposed for electrician coordination. Verify on site. Model dimensions are approximate.
1 / 3
SD07
black
sliding
deck
doors
Entry
W08
W14
W13
6.12 m
4.33 m
Desk 1
Desk 2
Record station
Books
Dahlia
sofa
Open
music
shelves
SMART Board
Amp
Guitars
FR
P1
D1
P2
D2
P3
D3
P4
P5
P6
P7
P8
Indicative ceiling data route
Power symbols P1–P8
Power/data are wall outlets. Symbols are offset for clarity. Wall coordinates and quantities appear on slide 3.
Data symbols D1–D3
2 × Cat6 at each desk and the SMART Board. Network source location to confirm.
One black glass-door fridge
Husky 130L beside the low bookcase under W13. Keep the power connection accessible.
Plan basis
Deck doors at left, entry at right. X runs left to right. Y runs from W14/W13 toward W08.
Notes: Concept drawing from office-design/index.html and user furniture requests, 25 September 2026. Room 6.12m by 4.33m is the supplied model, not a measured survey. Furniture shown schematically and electrical points are proposals. D1/D2/D3 each represent 2 Cat6 ports. Dashed blue lines indicate a conceptual ceiling data pathway and drops, not a wiring layout. Network source, containment, separation, capacity and final routing require site coordination by the relevant licensed trades. Existing electrical services are unknown. Both desks have a Samsung curved monitor and Mac mini. SMART Board source: https://downloads.smarttech.com/media/sitecore/en/support/product/sbfpd/7000series/specs/specssbid7275p.pdf. Fridge exact model and clearances require confirmation against the unit manual.

## Slide 2
Office ceiling and controls
Six recessed downlights with one central fan
Proposed for electrician coordination. Verify on site. Model dimensions are approximate.
2 / 3
SD07
black
sliding
deck
doors
Entry
W08
W14
W13
6.12 m
4.33 m
DL1
DL2
DL3
DL4
DL5
DL6
F1
S1
S2
DL1–DL6 Downlights
White recessed fittings. One dimmable group is proposed. Final output and beam angle to confirm.
F1 Central ceiling fan
Centre: X 3.06 m, Y 2.165 m. Render diameter: approximately 1.32 m. Separate fan control.
S1 / S2 Entry controls
S1: downlight dimmer.
S2: independent fan control.
On short wall return. Final position, height and door swing to confirm.
Downlight coordinates
X = 1.10, 3.06, 5.02 m
Y = 0.85 and 3.48 m
Notes: Ceiling concept matches office-design/index.html: six downlights at X 1.10, 3.06, 5.02m and Y 0.85, 3.48m. Fan centre X3.06m Y2.165m. Room origin is the deck/W14 corner. Nominal model ceiling height is 2.65m. Fan diameter in concept 1.32m. These are design coordinates, not construction setout. Electrician to coordinate structural mounting, fan blade and lighting clearances, ceiling construction and insulation, selected product instructions, dimmer compatibility and circuits on site. Controls shown beside the entry are proposed, and actual switch placement depends on door swing and access. No circuit specification or wiring design is supplied.

## Slide 3
Outlet schedule and site coordination
Quantities below are proposals for review with the electrician
Proposed for electrician coordination. Verify on site. Model dimensions are approximate.
3 / 3
ID | Location | Power sockets | Data | Plan X / Y (m) | Equipment
P1 / D1 | Desk 1 | 2 doubles = 4 | 2 × Cat6 | 1.80 / 0.00 | Samsung curved monitor, Mac mini, lamp + spare
P2 / D2 | Desk 2 | 2 doubles = 4 | 2 × Cat6 | 3.25 / 4.33 | Samsung curved monitor, Mac mini, lamp + spare
P3 / D3 | SMART Board | 2 doubles = 4 | 2 × Cat6 | 6.12 / 2.02 | Board, AV accessory and spare capacity
P4 | Record station | 2 doubles = 4 | — | 1.50 / 4.33 | Turntable, 2 Sonos Ones and audio accessory
P5 | Open music shelves | 2 doubles = 4 | — | 6.12 / 3.62 | Music gear and charging
P6 | Guitar / amp area | 1 double = 2 | — | 5.45 / 4.33 | Amplifier and pedal / accessory supply
P7 | 130L Husky fridge | 1 single = 1 | — | 4.30 / 0.00 | One accessible connection beside the fridge
P8 | Near entry | 1 double = 2 | — | 5.72 / 0.00 | Cleaning and general use
Proposed total: 25 sockets across 8 locations, plus 6 Cat6 ports
Confirm existing services, final mounting heights and cable routes on site. Keep outlets clear of the SMART Board mount, furniture backs and curtain hardware.
Fridge: allow 150 mm rear/sides/top provisionally. Confirm the actual unit manual and door swing.
Notes: Concept from office-design/index.html, geometry-notes.md, and user equipment list. Socket total = 4+4+4+4+4+2+1+2 = 25, comprising 12 double outlets and 1 single. Data total = 2+2+2 = 6 ports. Coordinates identify proposed approximate wall zones, not surveyed mounting positions or heights. X runs from the deck doors toward the entry wall, Y runs from W14/W13 toward W08. Diagram symbols have offsets for readability. Equipment and furniture footprints are schematic. Fridge body centre X4.850/Y0.4215m; proposed adjacent outlet P7 is at wall X4.30/Y0. The September 2026 official HUS130HDBLK specification confirms 541W x 543D x 840H mm. Exact owned unit has not been confirmed. Current specification gives 50–100mm optimal ventilation but the linked generic manual recommends 150mm around the unit. The concept conservatively holds 150mm at rear, sides and above, subject to the actual appliance instructions. Check connection accessibility, lead reach and entry/fridge door swings on site. Sources: https://www.huskybrand.com.au/products/glass-door-bar-fridge-black-hus130hdblk and https://www.huskybrand.com.au/cdn/shop/files/HUS130HDBLK_Spec-Sheet_c0b3010d-9aaf-4c68-93d0-15e9312304aa.pdf?v=13683754392081297532 . SMART Board source: https://downloads.smarttech.com/media/sitecore/en/support/product/sbfpd/7000series/specs/specssbid7275p.pdf. Existing services, circuit design, final heights, protection, cable separation and routes remain for on-site review by the electrician and relevant licensed trades. No powered blind or curtain feed is included; coordinate one separately if motorised coverings are chosen.